## Slide 1: Unit Commitment

## Slide 2: Economic Dispatch: Problem Definition
Given load
Given set of units on-line
How much should each unit generate to meet this load at minimum cost?
A
B
C
L

## Slide 3: Typical summer and winter loads

## Slide 4: Unit Commitment
Given load profile (e.g. values of the load for each hour of a day)
Given set of units available
When should each unit be started, stopped and how much should it generate to meet the load at minimum cost?
G
G
G
Load Profile
?
?
?

## Slide 5: A Simple Example
Unit 1:
    PMin = 250 MW, PMax = 600 MW
    C1 = 510.0 + 7.9 P1 + 0.00172 P12 $/h
Unit 2:
    PMin = 200 MW, PMax = 400 MW
    C2 = 310.0 + 7.85 P2 + 0.00194 P22 $/h
Unit 3:
    PMin = 150 MW, PMax = 500 MW
    C3 = 78.0 + 9.56 P3 + 0.00694 P32 $/h
What combination of units 1, 2 and 3 will produce 550 MW at minimum cost?
How much should each unit in that combination generate?

## Slide 6: Cost of the various combinations

## Slide 7: Observations on the example:
Far too few units committed: Can’t meet the demand
Not enough units committed: Some units operate above optimum
Too many units committed: Some units below optimum
Far too many units committed: Minimum generation exceeds demand
No-load cost affects choice of optimal combination

## Slide 8: A more ambitious example
Optimal generation schedule for a load profile
Decompose the profile into a set of period
Assume load is constant over each period
For each time period, which units should be committed to generate at minimum cost during that period?
Load
Time
12
6
0
18
24
500
1000

## Slide 9: Optimal combination for each hour

## Slide 10: Matching the combinations to the load
Load
Time
12
6
0
18
24
Unit 1
Unit 2
Unit 3

## Slide 11: Issues
Must consider constraints
  Unit constraints
  System constraints
Some constraints create a link between periods
Start-up costs
  Cost incurred when we start a generating unit
  Different units have different start-up costs
Curse of dimensionality

## Slide 12: Unit Constraints
Constraints that affect each unit individually:
  Maximum generating capacity
  Minimum stable generation
  Minimum “up time”
  Minimum “down time”
  Ramp rate

## Slide 13: Notations
Status of unit i at period t
Power produced by unit i during period t
Unit i is on during period t
Unit i is off during period t

## Slide 14: Minimum up- and down-time
Minimum up time
  Once a unit is running it may not be shut down immediately:
Minimum down time
  Once a unit is shut down, it may not be started immediately

## Slide 15: Ramp rates
Maximum ramp rates
  To avoid damaging the turbine, the electrical output of a unit cannot change by more than a certain amount over a period of time:
Maximum ramp up rate constraint:
Maximum ramp down rate constraint:

## Slide 16: System Constraints
Constraints that affect more than one unit
  Load/generation balance
  Reserve generation capacity
  Emission constraints
  Network constraints

## Slide 17: Load/Generation Balance Constraint

## Slide 18: Reserve Capacity Constraint
Unanticipated loss of a generating unit or an interconnection causes unacceptable frequency drop if not corrected rapidly
Need to increase production from other units to keep frequency drop within acceptable limits
Rapid increase in production only possible if committed units are not all operating at their maximum capacity

## Slide 19: How much reserve?
Protect the system against “credible outages”
Deterministic criteria:
  Capacity of largest unit or interconnection
  Percentage of peak load
Probabilistic criteria:
  Takes into account the number and size of the committed units as well as their outage rate

## Slide 20: Types of Reserve
Spinning reserve
  Primary
    Quick response for a short time
  Secondary
    Slower response for a longer time
Tertiary reserve
  Replace primary and secondary reserve to protect against another outage
  Provided by units that can start quickly (e.g. open cycle gas turbines)
  Also called scheduled or off-line reserve

## Slide 21: Cost of Reserve
Reserve has a cost even when it is not called
More units scheduled than required
  Units not operated at their maximum efficiency
  Extra start up costs
Must build units capable of rapid response
Cost of reserve proportionally larger in small systems
    Important driver for the creation of interconnections between systems

## Slide 22: Example
4th Unit Out

## Slide 23: Environmental constraints
Scheduling of generating units may be affected by environmental constraints
Constraints on pollutants such SO2, NOx
  Various forms:
    Limit on each plant at each hour
    Limit on plant over a year
    Limit on a group of plants over a year
Constraints on hydro generation
  Protection of wildlife
  Navigation, recreation

## Slide 24: Network Constraints
Transmission network may have an effect on the commitment of units
  Some units must run to provide voltage support
  The output of some units may be limited because their output would exceed the transmission capacity of the network
Cheap generators
May be “constrained off”
More expensive generator
May be “constrained on”
A
B

## Slide 25: Start-up Costs
Thermal units must be “warmed up” before they can be brought on-line
Warming up a unit costs money
Start-up cost depends on time unit has been off
tiOFF
αi
αi + βi

## Slide 26: Start-up Costs
Need to “balance” start-up costs and running costs
Example:
  Diesel generator: low start-up cost, high running cost
  Coal plant: high start-up cost, low running cost
Issues:
  How long should a unit run to “recover” its start-up cost?
  Start-up one more large unit or a diesel generator to cover the peak?
  Shutdown one more unit at night or run several units part-loaded?

## Slide 27: Summary
Some constraints link periods together
Minimizing the total cost (start-up + running) must be done over the whole period of study
Generation scheduling or unit commitment is a more general problem than economic dispatch
Economic dispatch is a sub-problem of generation scheduling

## Slide 28: Flexible Plants
Power output can be adjusted (within limits)
Examples:
  Coal-fired
  Oil-fired
  Open cycle gas turbines
  Combined cycle gas turbines
  Hydro plants with storage
Status and power output can be optimized
Thermal units

## Slide 29: Inflexible Plants
Power output cannot be adjusted for technical or commercial reasons
Examples:
  Nuclear
  Run-of-the-river hydro
  Renewables (wind, solar,…)
  Combined heat and power (CHP, cogeneration)
Output treated as given when optimizing

## Slide 30: Solving the Unit Commitment Problem
Decision variables:
  Status of each unit at each period:
  Output of each unit at each period:
Combination of integer and continuous variables

## Slide 31: How many combinations are there?
Examples
  3 units: 8 possible states
  N units: 2N possible states
111
110
101
100
011
010
001
000

## Slide 32: How many solutions are there anyway?
1
2
3
4
5
6
T=
Optimization over a time horizon divided into intervals
A solution is a path linking one combination at each interval
How many such paths are there?

## Slide 33: How many solutions are there anyway?
1
2
3
4
5
6
T=
Optimization over a time horizon divided into intervals
A solution is a path linking one combination at each interval
How many such path are there?
Answer:

## Slide 34: The Curse of Dimensionality
Example: 5 units, 24 hours
Processing 109 combinations/second, this would take 1.9 1019 years to solve
There are 100’s of units in large power systems...
Many of these combinations do not satisfy the constraints

## Slide 35: How do you Beat the Curse?
Brute force approach won’t work!
Need to be smart
Try only a small subset of all combinations
Can’t guarantee optimality of the solution
Try to get as close as possible within a reasonable amount of time

## Slide 36: Main Solution Techniques
Characteristics of a good technique
  Solution close to the optimum
  Reasonable computing time
  Ability to model constraints
Priority list / heuristic approach
Dynamic programming
Lagrangian relaxation

## Slide 37: A Simple Unit Commitment Example

## Slide 38: Unit Data
Unit | Pmin (MW) | Pmax (MW) | Min up (h) | Min down (h) | No-load cost ($) | Marginal cost ($/MWh) | Start-up cost ($) | Initial status
A | 150 | 250 | 3 | 3 | 0 | 10 | 1,000 | ON
B | 50 | 100 | 2 | 1 | 0 | 12 | 600 | OFF
C | 10 | 50 | 1 | 1 | 0 | 20 | 100 | OFF

## Slide 39: Demand Data
Reserve requirements are not considered

## Slide 40: Feasible Unit Combinations (states)
Combinations |  |  | Pmin | Pmax
A | B | C |  | 
1 | 1 | 1 | 210 | 400
1 | 1 | 0 | 200 | 350
1 | 0 | 1 | 160 | 300
1 | 0 | 0 | 150 | 250
0 | 1 | 1 | 60 | 150
0 | 1 | 0 | 50 | 100
0 | 0 | 1 | 10 | 50
0 | 0 | 0 | 0 | 0
 | 1 | 2 | 3
 | 150 | 300 | 200

## Slide 41: Transitions between feasible combinations
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State

## Slide 42: Infeasible transitions: Minimum down time of unit A
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State
 | TD | TU
A | 3 | 3
B | 1 | 2
C | 1 | 1

## Slide 43: Infeasible transitions: Minimum up time of unit B
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State
 | TD | TU
A | 3 | 3
B | 1 | 2
C | 1 | 1

## Slide 44: Feasible transitions
A | B | C
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
0 | 1 | 1
 | 1 | 2 | 3
Initial State

## Slide 45: Operating costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7

## Slide 46: Economic dispatch
State | Load | PA | PB | PC | Cost
1 | 150 | 150 | 0 | 0 | 1500
2 | 300 | 250 | 0 | 50 | 3500
3 | 300 | 250 | 50 | 0 | 3100
4 | 300 | 240 | 50 | 10 | 3200
5 | 200 | 200 | 0 | 0 | 2000
6 | 200 | 190 | 0 | 10 | 2100
7 | 200 | 150 | 50 | 0 | 2100
Unit | Pmin | Pmax | No-load cost | Marginal cost
A | 150 | 250 | 0 | 10
B | 50 | 100 | 0 | 12
C | 10 | 50 | 0 | 20

## Slide 47: Operating costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$1500
$3500
$3100
$3200
$2000
$2100
$2100

## Slide 48: Start-up costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$1500
$3500
$3100
$3200
$2000
$2100
$2100
Unit | Start-up cost
A | 1000
B | 600
C | 100
$0
$0
$0
$0
$0
$600
$100
$600
$700

## Slide 49: Accumulated costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$1500
$3500
$3100
$3200
$2000
$2100
$2100
$1500
$5100
$5200
$5400
$7300
$7200
$7100
$0
$0
$0
$0
$0
$600
$100
$600
$700

## Slide 50: Total costs
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
4
3
2
5
6
7
$7300
$7200
$7100
Lowest total cost

## Slide 51: Optimal solution
1 | 1 | 1
1 | 1 | 0
1 | 0 | 1
1 | 0 | 0
1
2
5
$7100

## Slide 52: Notes
This example is intended to illustrate the principles of unit commitment
Some constraints have been ignored and others artificially tightened to simplify the problem and make it solvable by hand
Therefore it does not illustrate the true complexity of the problem
The solution method used in this example is based on dynamic programming. This technique is no longer used in industry because it only works for small systems (< 20 units)

## Slide 53: Dynamic Programming Method
The recursive algorithm to compute the minimum cost in hour K with combination I is
Fcost = min{Pcost(K,I)+Scost{K-1,L:K,I} + Fcost(K-1,L)}
Fcost(K, I) = least total cost to arrive at state (K, I)
Pcost(K,I) = production cost for state (K, I)
Scost{K-1,L:K,I} = transition cost from state (K - 1, L) to state (K, I)

## Slide 54
Start
K=1
K=K+1
Fcost (K,I)= min{Pcost(K,I)+Scost{K-1,L:K,I}}
{L}=”N” feasible states in interval K-1
Fcost (K,I)= min{Pcost(K,I)+Scost{K-1,L:K,I} + Fcost(K-1,L)}
Save N lowest cost strategies
K=M Last Hours
Trace Optimal Schedule
X= Do for all states I in period K
X= Do for all states I in period K